## Slide 1: Distributed Energy Resource Model of the UNH-Microgrid
By Matthew Dodge

## Slide 2: Abstract
In today's world the push to use more clean energy in the power grid is higher than ever before. This is important for reducing the effect nonrenewable forms of energy have on our climate and environment, as well as the ability to meet the ever-increasing demand of electricity in our society. However, renewable Energy Sources such as wind or solar, are often intermittent since their efficiency depends on outside stimuli such as wind speed or the amount of sunlight present. Understanding the role and affect renewable energy resources have on existing grid infrastructure and their intermittent behavior is an important thing to know for engineers looking to improve and maintain the grid. This Project was designed to model the base case of the Oyster River Clean Innovation project which improves the UNH-Microgrid by adding 3MW of Solar Power, and a 2MW/8MWh Battery Energy Storage System to the existing grid infrastructure, using the Simscape Power systems toolbox in MATLAB Simulink. All forms Distributed Energy Resources were successfully modeled in MATLAB as individual systems, including the Photovoltaic arrays and the 3 existing turbine generators. However, the model struggled when these resources were connected to a model of the Grid load structure, also produced in Simulink.

## Slide 3: Introduction
The University of New Hampshire has for a long time been committed to sustainability. In maintenance of this effort, UNH has been working with Eversource, and the Town of Durham on the Oyster River Clean Innovation Project. The base case of this project is designed to try and improve grid reliability and resiliency by incorporating renewable Distributed Energy Resources in the form Solar Power, as well as a Battery Energy Storage System. The Expectation is that these additions will allow the UNH Microgrid to cover approximately 85 of annual operating hours without the need of Power from the Centralized grid. In an effort to better understand how these resources work and how it will affect grid performance I have made a model Each of the Existing, and future Distributed Energy Resources, as well as a model of the Grid Load structure.

## Slide 4: Design Goals
Successfully Model Each Individual Distributed Energy Resource in MATLAB
  (2 Photovoltaic Arrays : 1MW, 2MW), 3 Turbine Generators, 1Battery Energy Storage System
Be able to demonstrate the Distributed Energy Resources in a grid environment under various stimuli, such as temperature, solar irradiance, and changing electrical loads.
  Build a model of the Grid Load infrastructure, with dynamic load

## Slide 5: Modeling the existing Grid Infrastructure
4.6MW Solar Turbine, 7.9 MW Cogeneration Plant, .595 MW Louis Allis Steam Turbine

## Slide 6: The Turbines
The 3 Turbine generators were effectively modeled the same way with slight changes made to account for the difference in MW and KV output.
Utilizes a Steam Turbine Governor Block to feedback and position control the motion of the armature in the Simplified Synchronous machine
  Fed into a transformer to step up the voltage to the desired ex. 4160Vto 34.5 KV
Voltage and Current measurements are then taken on the output.

## Slide 7: Modeling the Future Grid Infrastructure
2MW UNH PV Array, 1MW WWTF PV array P,
2 MW/8Mwh BESS System

## Slide 8: The Photovoltaics/BESS
The UNH PV array model and the Battery Energy storage System were combined into the same model for ease of use since they are often utilized together for charging and discharging
PV Array:
Utilized the PV block in Simulink
  Made array that was capable of desired Wattage
  Made three phase inverter circuit that converted the high voltage DC to 3-Phase AC then to a Transformer.
BESS
Utilized the battery block in Simulink
  Specified the capacity, state of charge, MWh
  Controls capable of modeling charging and discharging
  Not Technically tuned to for Peak shaving control

## Slide 9: Modeling the Grid Load Infrastructure
The 12 Circuits that make up the UNH Microgrid

## Slide 10: Modeling any Parameter
By Using a Load profile data stored in and excel executing a Single MATLAB script and spread sheet at the Beginning of the Simulation the Grid can be Made to represent any Load Profile, any temp, and any sun Irradiance from 2015 to 2017.

## Slide 11: The Full Model

## Slide 12: Results
Successfully made MATLAB Simulink models of every DER
Was able to create a Grid Load that was adaptable to account for the variability that occurs when using Renewable Resources.
The sources when all connected to the Grid Load Model did not function as planned.
  Simulations are also slow even for short time scales

## Slide 13: Acknowledgements
Dr. Nicholas Kirsch- For being this projects advisor and meeting on a weekly and biweekly basis, to discuss progress and give advice to that helped further the project development
Matt O’Keefe- As the director of energy and utilities at UNH Matt was very helpful in providing documentation and information about the grid such as One-line schematics, or Load data which were critical to this project.

## Slide 14: References
https://www.mathworks.com/help/physmod/sps/ug/steam-turbine-and-governor-system-subsynchronous-resonance.html
Various Math Works Forums